## Air Handler - Front Return
Air Handler Front Return
Models |  |  | BFR18B15S2T5 | BFR24B15S2T5 | BFR30B15S2T5 | BFR3615S2T5
Power supply |  | V/Ph/Hz | 208/230/1/60 | 208/230/1/60 | 208/230/1/60 | 208/230/1/60
Cooling | Capacity | Btu/h | 17000 | 22000 | 28000 | 33000
Indoor external static pressure |  | Pa | 145 | 145 | 145 | 145
Throttle type |  |  | orifice | orifice | orifice | orifice
Indoor coil | Number of row |  | 5 | 5 | 5 | 5
| Tube pitch(a) x row pitch(b) | in | 0.83×0.53 | 0.83×0.53 | 0.83×0.53 | 0.83×0.53
| Fin spacing | in | 0.059 | 0.059 | 0.059 | 0.059
| Fin material |  | Hydrophilic Aluminium Fin | Hydrophilic Aluminium Fin | Hydrophilic Aluminium Fin | Hydrophilic Aluminium Fin
| Tube outside diameter | mm | Ф7 | Ф7 | Ф7 | Ф7
| Tube type |  | Inner Grooved | Inner Grooved | Inner Grooved | Inner Grooved
| Coil length x height x width | in | 16.97×18.2×2.63 | 16.97×18.2×2.63 | 17.44×23.15×2.63 | 17.44×23.15×2.63
| Number of circuit |  | 6 | 6 | 8 | 8
| Type |  | ECM | ECM | ECM | ECM
| Input | W | 166 | 221 | 267 | 267
| Output | W | 249 | 249 | 373 | 373
| Full load amps(FLA) | A | 1.6 | 2.2 | 2.4 | 2.7
| Capacitor | μF | / | / | / | /
| Speed | rpm | 900/935/960/1010/1050 | 900/935/960/1010/1050 | 895/930/960/1000/1030 | 895/930/960/1000/1030
Blower | Diameter | in | 11 | 11 | 11 | 11
| Width | in | 6 | 6 | 10 | 10
Indoor air flow |  | CFM | 715 | 850 | 1020 | 1145
Indoor sound pressure level |  | dB(A) | 47-57 | 47-57 | 48-58 | 48-58
Indoor dimension | Unit (W×D×H) | in | 20-1/2×15×36 | 20-1/2×15×36 | 22×19-1/10×39-3/5 | 22×19-1/10×39-3/5
|  | mm | 522×381×915 | 522×381×915 | 559×485×1006 | 559×485×1006
| Packing (W×D×H) | in | 23-1/5×17-7/10×39-2/5 | 23-1/5×17-7/10×39-2/5 | 24-3/5×21-3/5×42-9/10 | 24-3/5×21-3/5×42-9/10
|  | mm | 590×450×1000 | 590×450×1000 | 625×550×1090 | 625×550×1090
| Net / Gross weight | kg | 40/44 | 40/44 | 51/56 | 51/56
|  | lbs | 88/97 | 88/97 | 112/123 | 112/123
Refrigerant pipe | Liquid side | in | 3/8 | 3/8 | 3/8 | 3/8
| Gas side | in | 3/4 | 3/4 | 3/4 | 3/4
Shipping per STD 20/40/40HQ |  |  | 100/200/200 | 100/200/200 | 72/156/156 | 72/156/156