## AIR HANDLER - MULTIPOSITION
AIR HANDLER - MULTIPOSITION
Model |  |  | BAH18B15S2R5 | BAH24B15S2R5 | BAH30B15S2R5 | BAH36B15S2R5 | BAH42B15S2R5 | BAH48B15S2R5 | BAH60B15S2R5
Power supply |  | V/Ph/Hz | 208~230V/1N/60Hz | 208~230V/1N/60Hz | 208~230V/1N/60Hz | 208~230V/1N/60Hz | 208~230V/1N/60Hz | 208~230V/1N/60Hz | 208~230V/1N/60Hz
Indoor external static pressure |  | Pa | 145 | 145 | 145 | 145 | 145 | 145 | 145
Throttle type |  |  | piston | piston | piston | piston | piston | piston | piston
MCA |  | A | 4 | 4 | 5 | 5 | 7 | 7 | 7
MOP |  | A | 6 | 6 | 6 | 6 | 10 | 10 | 10
Indoor coil | Number of row |  | 3(row)×2(piece) | 3(row)×2(piece) | 4(row)×2(piece) | 4(row)×2(piece) | 4(row)×2(piece) | 5(row)×2(piece) | 5(row)×2(piece)
| Tube pitch(a)xrow pitch(b) | in | 0.83×0.53 | 0.83×0.53 | 0.83×0.53 | 0.83×0.53 | 0.83×0.53 | 0.83×0.53 | 0.83×0.53
| Fin spacing | in | 1/16 | 1/16 | 1/16 | 1/16 | 1/16 | 1/16 | 1/16
| Fin material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
| Tube outside diameter | in | Ф 0.276 | Ф 0.276 | Ф 0.276 | Ф 0.276 | Ф 0.276 | Ф 0.276 | Ф 0.276
| Tube material |  | inner grooved | inner grooved | inner grooved | inner grooved | inner grooved | inner grooved | inner grooved
| Coil length x height x width | in | 17 5/8×14 7/8×1 5/8 | 17 5/8×14 7/8×1 5/8 | 16 1/2×17 1/2×2 1/8 | 16 1/2×17 1/2×2 1/8 | 17 7/16×16 17/32×2 7/64 | 19 27/32×21 1/2×2 5/8 | 19 27/32×21 1/2×2 5/8
| Number of circuit |  | 6 | 6 | 8 | 8 | / | / | /
| Type |  | ECM | ECM | ECM | ECM | ECM | ECM | ECM
| Model |  | DZJ-249F-12 | DZJ-249F-12 | DZJ-373F-12 | DZJ-373F-12 | DZJ-560F-12 | DZJ-560F-12 | DZJ-560F-12
| Rate current | A | 2.6 | 2.6 | 3.8 | 3.8 | 5.4 | 5.4 | 5.4
| Input | W | 142.4 | 142.4 | 245.9 | 245.9 | 249.3 | 249.3 | 249.3
| Output | W | 249 | 249 | 373 | 373 | 560 | 560 | 560
| Capacitor | μF | / | / | / | / | / | / | /
| Speed (Hi/Me/Lo) | rpm
| Speed (Hi/Me Hi/Me/Me lo/Lo) 5/4/3/2/1 | RPM | 643/593/556/476/412 | 643/593/556/476/412 | 760/718/662/610/548 | 760/718/662/610/548 | 977/833/760/683/610 | 977/833/760/683/610 | 977/833/760/683/610
Blower | diameter | in | 12.3125 | 12.3125 | 12.3125 | 12.3125 | 12.3125 | 12.3125 | 12.3125
| width | in | 12.9062 | 12.9062 | 12.9062 | 12.9062 | 12.9062 | 12.9062 | 12.9062
Indoor air flow |  | CFM | 770 | 785 | 975 | 1030 | 1230 | 1363 | 1580
Indoor noise level |  | dB(A) | 50 | 54 | 56 | 56 | 59 | 59 | 60
Indoor dimension | Unit (WxHxD) | in | 19-5/8×45-3/4×22 | 19-5/8×45-3/4×22 | 19-5/8×45-3/4×22 | 19-5/8×45-3/4×22 | 22×53-1/8×24-1/2 | 22×53-1/8×24-1/2 | 22×53-1/8×24-1/2
|  | mm | 500×1162×560 | 500×1162×560 | 500×1162×560 | 500×1162×560 | 560×1350×623 | 560×1350×623 | 560×1350×623
| Packing (WxHxD) | in | 22-5/6×47-5/8×25-3/5 | 22-5/6×47-5/8×25-3/5 | 22-5/6×47-5/8×25-3/5 | 22-5/6×47-5/8×25-3/5 | 28×54-3/4×25-1/5 | 28×54-3/4×25-1/5 | 28×54-3/4×25-1/5
|  | mm | 580×1210×650 | 580×1210×650 | 580×1210×650 | 580×1210×650 | 710×1390×640 | 710×1390×640 | 710×1390×640
| Net / Gross weight | kg | 56/61.5 | 56/61.5 | 60/63.5 | 60/63.5 | 72/78 | 72/78 | 77/83
|  | lbs | 123/135 | 123/135 | 132/140 | 132/140 | 159/172 | 159/172 | 170/183
Shipping per STD 20/40/40HQ |  |  | 30/60/120 | 30/60/120 | 30/60/120 | 30/60/120 | 30/60/120 | 27/54/54 | 27/54/54