## Condenser - Cooling Only
Condenser Cooling Only
Models |  |  | BAC18B15S2T5 | BAC24B15S2T5 | BAC30B15S2T5 | BAC36B15S2T5 | BAC42B15S2T5 | BAC48B15S2T5 | BAC60B15S2T5
Outdoor power supply |  | V/Ph/Hz | 208/230/1/60 | 208/230/1/60 | 208/230/1/60 | 208/230/1/60 | 208/230/1/60 | 208/230/1/60 | 208/230/1/60
Cooling | Capacity | Btu/h | 17000 | 22000 | 28000 | 33000 | 40000 | 45000 | 54000
| Input | W | 1500 | 1930 | 2272 | 2800 | 3420 | 3623 | 4649
| EER2 | Btu/h.W | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.5 | 11.2
| SEER2 (AHRI Certified) | Btu/h.W | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14
Heating | Capacity | Btu/h | － | － | － | － | － | － | －
| HSPF2 (AHRI Certified) | Btu/h.W | － | － | － | － | － | － | －
Max. input consumption |  | W | 2250 | 3050 | 3300 | 4455 | 5430 | 6000 | 7300
Max. current |  | A | 20 | 25 | 30 | 35 | 35 | 45 | 50
Compressor | Brand |  | LG | LG | LG | LG | LG | LG | LG
| Model |  | YPH016KAA | YPH020KAA | YPH024KAA | YPH029KAA | YPH036KAA | YBH039KAA | YBH049KAA
| Type |  | scroll | scroll | scroll | scroll | scroll | scroll | scroll
| Capacity | Btu/h | 19500 | 24800 | 29700 | 36000 | 44700 | 48500 | 61400
| Input | W | 1192 | 1498 | 1772 | 2134 | 2684 | 2877 | 3664
| Rated current (RLA) | A | 9.3 | 12.1 | 14.8 | 18.2 | 19.4 | 23.1 | 28.1
| Locked rotor Amp (LRA) | A | 47 | 50 | 71 | 75 | 96 | 95 | 125
| Thermal protector | uf | 35 | 35 | 40 | 45 | 45 | 70 | 70
| Refrigerant oil | ml | 740 | 740 | 740 | 740 | 740 | 1280 | 1280
| Type |  | AC | AC | AC | AC | AC | AC | AC
| Input | W | 162 | 162 | 222 | 230 | 230 | 370 | 370
| Output | W | 85 | 85 | 160 | 110 | 110 | 230 | 230
| Full load amps (FLA) | A | 1 | 0.9 | 1.2 | 1 | 1 | 2 | 2.3
| Capacitor | μF | 6 | 6 | 6 | 6 | 6 | 12 | 12
| Speed | rpm | 970 | 970 | 1100 | 850 | 850 | 1110 | 1110
Outdoor coil | Number of row |  | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Fin spacing | in | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556
| Fin material |  | Hydrophilic Aluminium Fin | Hydrophilic Aluminium Fin | Hydrophilic Aluminium Fin | Hydrophilic Aluminium Fin | Hydrophilic Aluminium Fin | Hydrophilic Aluminium Fin | Hydrophilic Aluminium Fin
| Tube outside diameter | mm | Ф 7 | Ф 7 | Ф 7 | Ф 7 | Ф 7 | Ф 7 | Ф 7
| Tube type |  | Inner Grooved | Inner Grooved | Inner Grooved | Inner Grooved | Inner Grooved | Inner Grooved | Inner Grooved
| Coil length x height x width | in | 61.7×23.15×1.05 | 61.7×23.15×1.05 | 61.7×23.15×1.05 | 83.8×23.15×1.05 | 83.8×31.48×1.05 | 83.8×31.48×1.05 | 83.8×31.48×1.05
| Number of circuit |  | 6 | 6 | 6 | 6 | 10 | 10 | 10
Outdoor air flow |  | CFM | 2000 | 2000 | 2250 | 2750 | 3300 | 4000 | 4000
Outdoor sound pressure level |  | dB(A) | 60 | 60 | 63 | 63 | 65 | 65 | 63
Outdoor dimension | Unit (W×D×H) | in | 23-3/5×23-3/5×25 | 23-3/5×23-3/5×25 | 23-3/5×23-3/5×25 | 29-1/7×29-1/7×25 | 29-1/7×29-1/7×32-7/8 | 29-1/7×29-1/7×32-7/8 | 29-1/7×29-1/7×32-7/8
|  | mm | 600×600×635 | 600×600×635 | 600×600×635 | 740×740×635 | 740×740×835 | 740×740×835 | 740×740×835
| Packing (W×D×H) | in | 25×25×26-1/5 | 25×25×26-1/5 | 25×25×26-1/5 | 30-1/2×30-1/2×26-1/5 | 30-1/2×30-1/2×34-1/10 | 30-1/2×30-1/2×34-1/10 | 30-1/2×30-1/2×34-1/10
|  | mm | 635×635×665 | 635×635×665 | 635×635×665 | 775×775×665 | 775×775×865 | 775×775×865 | 775×775×865
| Net / Gross weight | kg | 61.3/64.3 | 61.1/64.1 | 62.2/65.2 | 71.6/75.6 | 86.3/90.8 | 94.8/99.3 | 95.4/99.9
|  | lbs | 135.1/141.8 | 134.7/141.3 | 137.1/143.7 | 157.9/166.7 | 190.3/200.2 | 209/218.9 | 210.3/220.2
Refrigerant | Type |  | R454B
| Charging volume | kg/oz/lbs-oz | 2.2 / 77.6 / 4-14 | 2.47 / 87.1 / 5-7 | 2.5 / 88.2 / 5-8 | 2.8 / 98.8 / 6-3 | 3.5 / 123.4 / 7-11 | 3.66 / 129.1 / 8-1 | 3.5 / 123.5 / 7-12
Refrigerant pipe | Liquid side | in | Ф3/8 | Ф3/8 | Ф3/8 | Ф3/8 | Ф3/8 | Ф3/8 | Ф3/8
| Gas side | in | Ф3/4 | Ф3/4 | Ф3/4 | Ф3/4 | Ф3/4 | Ф7/8 | Ф7/8
| Max. refrigerant pipe length | ft | 150 | 150 | 150 | 150 | 150 | 150 | 150
| Max. difference in level | ft | 60 | 60 | 60 | 60 | 60 | 60 | 60
Design pressure |  | MPa | 4.3/1.7 | 4.3/1.7 | 4.3/1.7 | 4.3/1.7 | 4.3/1.7 | 4.3/1.7 | 4.3/1.7
Max. pressure |  | MPa | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
Operation temp range | Cooling | ℉ | 61-118 | 61-118 | 61-118 | 61-118 | 61-118 | 61-118 | 61-118
| Heating | ℉ | / | / | / | / | / | / | /
Shipping per STD 20/40/40HQ |  |  | 81/162/216 | 81/162/216 | 81/162/216 | 63/135/180 | 42/90/135 | 42/90/135 | 42/90/135

## Condenser - Heat Pump
Condenser Heat Pump
Models |  |  | BHP18B15S2T5 | BHP24B15S2T5 | BHP3015S2T5 | BHP3615S2T5 | BHP4215S2T5 | BHP4815S2T5 | BHP6015S2T5
Outdoor power supply |  | V/Ph/Hz | 208/230/1/60 | 208/230/1/60 | 208/230/1/60 | 208/230/1/60 | 208/230/1/60 | 208/230/1/60 | 208/230/1/60
Cooling | Capacity | Btu/h | 17000 | 22000 | 28000 | 33000 | 40000 | 45000 | 55000
| Input | W | 1520 | 1930 | 2305 | 2730 | 3340 | 3670 | 4665
| EER2 | Btu/h.W | 11.4 | 11.2 | 11.4 | 11.4 | 11.4 | 11.2 | 11.2
| SEER2 (AHRI Certified) | Btu/h.W | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3
Heating | Capacity | Btu/h | 17000 | 22000 | 26000 | 31000 | 41000 | 44000 | 53000
| HSPF2(AHRI Certified) | Btu/h.W | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Max. input consumption |  | W | 2250 | 3050 | 3300 | 4455 | 5430 | 6000 | 7300
Max. current |  | A | 20 | 25 | 30 | 35 | 35 | 45 | 50
Compressor | Brand |  | LG | LG | LG | LG | LG | LG | LG
| Model |  | YPH016KAA | YPH020KAA | YPH024KAA | YPH029KAA | YPH036KAA | YBH039KAA | YBH049KAA
| Type |  | scroll | scroll | scroll | scroll | scroll | scroll | scroll
| Capacity | Btu/h | 19500 | 24800 | 29700 | 36000 | 44700 | 48500 | 61400
| Input | W | 1192 | 1498 | 1772 | 2134 | 2684 | 2877 | 3664
| Rated current (RLA) | A | 9.3 | 12.1 | 14.8 | 18.2 | 19.4 | 23.1 | 27.8
| Locked rotor Amp (LRA) | A | 47 | 50 | 71 | 75 | 96 | 95 | 125
| Thermal protector | uf | 35 | 35 | 40 | 45 | 45 | 70 | 70
| Refrigerant oil | ml | 740 | 740 | 740 | 740 | 1280 | 1280 | 1280
| Model |  | AC | AC | AC | AC | AC | AC | DC
| Input | W | 162 | 162 | 222 | 230 | 230 | 370 | 300
| Output | W | 85 | 85 | 160 | 110 | 110 | 230 | 200
| Full load amps(FLA) | A | 1 | 0.9 | 1.2 | 1 | 1 | 2 | 2.5
| Capacitor | μF | 6 | 6 | 6 | 6 | 6 | 12 | /
| Speed | rpm | 970 | 970 | 1100 | 850 | 850 | 1110 | 1050
Outdoor coil | Number of row |  | 2 | 2 | 2 | 2 | 2 | 2 | 2.5
| Fin spacing | in | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556 | 0.055556
| Fin material |  | Hydrophilic Aluminium Fin | Hydrophilic Aluminium Fin | Hydrophilic Aluminium Fin | Hydrophilic Aluminium Fin | Hydrophilic Aluminium Fin | Hydrophilic Aluminium Fin | Hydrophilic Aluminium Fin
| Tube outside diameter | mm | Ф7 | Ф7 | Ф7 | Ф7 | Ф7 | Ф7 | Ф7
| Tube type |  | Inner Grooved | Inner Grooved | Inner Grooved | Inner Grooved | Inner Grooved | Inner Grooved | Inner Grooved
| Coil length x height x width | in | 61.7×23.15×1.05 | 61.7×23.15×1.05 | 61.7×23.15×1.05 | 83.8×23.15×1.05 | 83.8×31.48×1.05 | 83.8×31.48×1.05 | 83.8×31.48×1.58
| Number of circuit |  | 6 | 6 | 6 | 6 | 10 | 10 | 8
Outdoor air flow |  | CFM | 2000 | 2000 | 2250 | 2750 | 3300 | 4000 | 4000
Outdoor sound pressure level |  | dB(A) | 60 | 60 | 63 | 63 | 65 | 65 | 63
Outdoor dimension | Unit (W×D×H) | in | 23-3/5×23-3/5×25 | 23-3/5×23-3/5×25 | 23-3/5×23-3/5×25 | 29-1/7×29-1/7×25 | 29-1/7×29-1/7×32-7/8 | 29-1/7×29-1/7×32-7/8 | 29-1/7×29-1/7×32-7/8
|  | mm | 600×600×635 | 600×600×635 | 600×600×635 | 740×740×635 | 740×740×835 | 740×740×835 | 740×740×835
| Packing (W×D×H) | in | 25×25×26-1/5 | 25×25×26-1/5 | 25×25×26-1/5 | 30-1/2×30-1/2×26-1/5 | 30-1/2×30-1/2×34-1/10 | 30-1/2×30-1/2×34-1/10 | 30-1/2×30-1/2×34-1/10
|  | mm | 635×635×665 | 635×635×665 | 635×635×665 | 775×775×665 | 775×775×865 | 775×775×865 | 775×775×865
| Net / Gross weight | kg | 65.4/68.4 | 65.3/68.3 | 66.2/69.2 | 78.5/82.5 | 92/96.5 | 100.4/104.9 | 104.4/108.9
|  | lbs | 144.2/150.8 | 144/150.6 | 146/152.6 | 173.1/181.9 | 202.8/212.8 | 221.3/231.3 | 229/240
Refrigerant | Type |  | R454B
| Charging volume | kg/oz/lbs-oz | 2.3 / 81.1 / 5-1 | 2.6 / 91.7 / 5-12 | 2.6 / 91.7 / 5-12 | 2.85 / 100.5 / 6-4 | 3.65 / 128.8 / 8-1 | 3.85 / 135.8 / 8-8 | 4.6 / 162.3 / 10-2
Refrigerant pipe | Liquid side | in | Ф3/8 | Ф3/8 | Ф3/8 | Ф3/8 | Ф3/8 | Ф3/8 | Ф3/8
| Gas side | in | Ф3/4 | Ф3/4 | Ф3/4 | Ф3/4 | Ф3/4 | Ф7/8 | Ф7/8
| Max. refrigerant pipe length | ft | 150 | 150 | 150 | 150 | 150 | 150 | 150
| Max. difference in level | ft | 60 | 60 | 60 | 60 | 60 | 60 | 60
Design pressure |  | MPa | 4.3/1.7 | 4.3/1.7 | 4.3/1.7 | 4.3/1.7 | 4.3/1.7 | 4.3/1.7 | 4.3/1.7
Max. pressure |  | MPa | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
Operation temp range | Cooling | ℉ | 61-118 | 61-118 | 61-118 | 61-118 | 61-118 | 61-118 | 61-118
| Heating | ℉ | 17-80 | 17-80 | 17-80 | 17-80 | 17-80 | 17-80 | 17-80
Shipping per STD 20/40/40HQ |  |  | 81/162/216 | 81/162/216 | 81/162/216 | 63/135/180 | 42/90/135 | 42/90/135 | 42/90/135
.